## Slide 1
One Energy portal
&
Pulse Secure
Jordan Swift
10/19/2018

## Slide 2: Typical wind farm
Not secure – Servers on Public Facing IPs

## Slide 3: Public facing IP = Hacker’s dream

## Slide 4: Port scan potential target

## Slide 5: Password cracker for the rest
111.202.252.34:6969

## Slide 6: One Energy wind farm - NFWC

## Slide 7: Port scan potential target - ball

## Slide 8: NO Luck despite ports open
74.142.20485:80

## Slide 9: VPN connection
Virtual Private Network (VPN) – establish a virtual point-to-point “tunneling” connection through the use of dedicated connections.
  Tunnel between the local and remote device, and ensures a secure communication between them.
  The VPN connection is only established when the client device authenticates itself on the VPN server

## Slide 10: This would work?
A VPN connection would need to be made for accessing each project. Problem: Only 1 VPN connection per computer. Cooper and Haviland are an example of this

## Slide 11: Dynamic Multipoint VPN
Allows “spokes” to communicate directly with each other over the internet.
Each location has a configuration to connect to the VPN device (hub).
Once user login into the hub they have the ability to access all “spokes” from their location without multiple VPN connections.

## Slide 12: One Energy Projects - spokes
A VPN connection can be made to central location with in Bluffton. That box is already had VPN connections to all other projects. This allows for all projects to be accessed through one connection – Pulse Portal

## Slide 13: One Energy project layout

## Slide 14: One Energy project Networking diagram

## Slide 15: KEYpass is your friend

## Slide 16: One Energy Roles
ROLE | 2F | Accessibility
OE Low | No | LAN 1 Web Access Only (SCADA)
OE High | Yes | LAN 1 All Access and LAN 2 Web Access
OE Camera | No | LAN 2 Web Access
OE Operator | No | LAN 1, LAN 2, LAN 3, and LAN 4 Unrestricted
Goldwind Low | No | LAN 1 Web Access Only (SCADA)
Goldwind High | Yes | LAN 1 All Access & PLC Access
Goldwind Admin | Yes | LAN 1 All Access
Customer SCADA | No | LAN 1 Web Access Only (SCADA)

## Slide 17: Last Curveball – DUO (2F)

## Slide 18: Logging into Pulse Secure/ONE Energy portal
Pulse Secure
Open Pulse Connect Secure
Username/Password
One Energy Portal
login.seemyturbine.com/oneenergyduo
Username/Password

## Slide 19: Logging into Pulse Secure/ONE Energy portal
Pulse Secure
Type “Push”, “Call”, or Enter Duo Passcode
One Energy Portal
Click 1 of the 3 options

## Slide 20: Logging into Pulse Secure/ONE Energy portal
Push
Call
Passcode

## Slide 21: Logging into Pulse Secure/ONE Energy portal
Pulse Secure
Decide what Role to Access
One Energy Portal
Decide what Role to Access

## Slide 22: Logging into Pulse Secure/ONE Energy portal
Pulse Secure
Accessed Bluffton Hub – 10.1.2.1
One Energy Portal
Accessed One Energy Portal

## Slide 23: Accessing SCADA
Pulse Secure
Input IP Address into Internet Browser
One Energy Portal
Click SCADA Bookmark

## Slide 24: Remote access into Project server
Pulse Secure
Open RDP Protocol
Input Computer Name (IP Address)
Input Username/Password
One Energy Portal
Click Terminal Session
Input Username/Password

## Slide 25: Accessing Turbine PLC
Pulse Secure
Input IP Address into Internet Browser
One Energy Portal
Click PLC Bookmark

## Slide 26: Accessing Security system
Pulse Secure
Input IP Address into Internet Browser
One Energy Portal
Click Camera Bookmark

## Slide 27: Accessing relay/meter
Pulse Secure
Open AcSELerator Quickset
Input Relay/Meter IP Address
Input ACC and 2AC password
One Energy Portal
Access Operations Server - RDP
Open AcSELerator Quickset on the local Computer
Input Relay/Meter IP address – local IP
Input ACC and 2AC password

## Slide 28: Inside the Control equipment enclosure

## Slide 29
LAN 1 – Port 1
LAN 2 – Port 2
LAN 3 – Port 3
LAN 4 – Port 4
WAN – Port 0
ISP – Port 5

## Slide 30: Connection in CEE
LAN 1 = SCADA (Port 1)
  IP = 192.168.149.1 /22
  Subnet = 255.255.252.0
LAN 2 = Security (Port 2)
  IP = 192.168.95.1/28
  Subnet = 255.255.255.240
LAN 3 = System Operator (Port 3)
  IP = 192.168.10.1/24
  Subnet = 255.255.255.0
LAN 4 = MODBUS (Port 4)
  IP = 192.168.20.1/24
  Subnet = 255.255.255.0

## Slide 31: Changing your Computer IP
Normally your computer is set up for DHCP
  Dynamic Host Configuration Protocol
  Automatically provides a host with its IP address and other related configuration information – subnet mask, default gateway, and DNS.
  Reliable IP address configuration
  Reduced network administration
What is your IP?
  IPCONFIG /all

## Slide 32: Changing your Computer IP
Project Firewall’s are not set up for DHCP
  Will need to statically assign network settings to your computer
Will need to Statically assigned IP Address
  Dedicated IP address assigned to your machine
What is your IP?
  IPCONFIG /all

## Slide 33: Changing your Computer IP
Control Panel
  Network and Internet
    Network and Sharing Center
      Change adapter settings
        Right click on “Connection” and Select “Properties”
          Click on Internet Protocol Version 4 (TCP/IPv4)
            Select “Properties”
              Click “Use the following IP address”
                Input IP configuration and click “Ok”
Right Click on Ethernet/Wi-Fi
  Open Network & Internet Settings
    Change adapter settings
      Right click on “Connection” and Select “Properties”
        Click on Internet Protocol Version 4 (TCP/IPv4)
          Select “Properties”
            Click “Use the following IP address”
              Input IP configuration and click “Ok”

## Slide 34
OE Project
IP Configuration:
IP Address:
  192.168.50.2-255
Subnet mask:
  255.255.255.0
Default Gateway
  192.168.10.1
Preferred DNS server:
  8.8.8.8
Alternate DNS server:
  8.8.4.4

## Slide 35: Questions